POWER PLANT

ISSUE - I: March 2014

____________________________________________________________________________________________________________

SPECIFICATION ON

SMPS BASED POWER PLANT

No. : BSNL/Specification/SMP – 001/01/March.2014

BHARAT SANCHAR NIGAM LIMITED

(A Government of India Enterprise),

Bharat Sanchar Bhawan, Janpath, Website: www.bsnl.co.in

NEW DELHI – 110 001, INDIA

All Rights Reserved and no part of this publication may be reproduced, stored in a retrieval system or transmitted, in any form or means, electronic  or mechanical, photocopied, recorded, scanned, without written permission from the Bharat Sanchar Nigam Ltd., New Delhi (A Government of India Enterprise), Bharat Sanchar Bhawan, Janpath, New Delhi – 110 001. Website: www.bsnl.co.in

CONTENTS

| Clause No. | Description Of Items | Page No. |
| --- | --- | --- |
|  | History Sheet | 3 |
|  | References | 4 |
| PART 1 | TECHNICAL REQUIREMENTS | 5 |
| 1.0 | Scope | 6 |
| 1.2 | Functional & Technical requirements | 7 |
| 1.2.1 | Functional Requirements | 7 |
| 1.2.1.1 | Lightning and Surge Protection | 7 |
| 1.2.2 | Technical Requirements | 7 |
| 1.2.2.1 | System application | 8 |
| 1.2.2.2 | DSCA | 8 |
| 1.2.2.3 | Power plant compatibility with Engine Alternator | 9 |
| 1.2.2.4 | Load sharing (Parallel Operation) | 9 |
| 1.2.2.5 | Battery Monitoring | 9 |
| 1.2.2.6 | Protections | 11 |
| 1.2.2.7 | Monitoring/Alarm and Indicating Lamps | 12 |
| 1.2.2.8 | Remote control and monitoring | 13 |
| 1.2.2.9 | Electrical Requirements | 13 |
| 1.2.2.9.1.2 | Power Derating | 14 |
| 1.2.2.9.1.3 | Neutral Path Current | 14 |
| 1.2.3 | Power Plants compatible with Conventional batteries | 16 |
| 1.2.3.4 | Sleep Mode Operation | 18 |
| PART 2 | GENERAL REQUIREMENTS | 19 |
| 2.0 | General Requirements | 20 |
| 2.1 | RFI Suppression | 20 |
| 2.2 | Power Plant system configuration | 22 |
| 2.3 | Rack Configuration | 23 |
| 2.4 | Constructional Features | 23 |
| 2.4.1.9 | SMPS Power Plant System Ultimate Capacity | 24 |
| 2.5 | Accessibility | 26 |
| 2.6 | Terminations | 26 |
| 2.7 | Bus-bars | 27 |
| 2.8 | Cabling and wiring | 27 |
| 2.9 | Earthing | 27 |
| 2.10 | Mounting of Components and Lay out | 28 |
| 2.11 | Documentation | 28 |
| 2.12 | Quality Requirements | 29 |
| 2.13 | Name Plate | 31 |
| 2.14 | MTTR and MTBF | 31 |
| 2.15 | Field Observations | 32 |
| 2.16 | Packing | 32 |
| 2.17 | Environmental Requirements | 32 |
| PART 3 | GUIDELINES FOR THE PURCHASER/USER | 34 |
| 3.0 | Guidelines for the Purchaser/User | 35 |
| Annexure-1 | Protocol or Sequence of Exchange of Information between Power plant & Remote Site monitoring equipment | 36 |
| Annexure-2 | Ordering Information | 45 |
|  | Abbreviations | 46 |

HISTORY SHEET

| Sr. No. | Name of the Generic Requirements | No. of the Generic Requirements | Remarks |
| --- | --- | --- | --- |
| 1 | SMPS Based Power Plants | G/SMP-01/01 JUL 94 | First issue |
| 2 | SMPS Based Power Plants | G/SMP-01/02 SEP 96 | Second issue |
| 3 | SMPS Based Power Plants | G/SMP-01/03 MAR 97 | Third issue |
| 4 | SMPS Based Power Plants | GR/SMP-01/04 FEB 2001 | Fourth issue |
| 5 | SMPS Based Power Plants | GR/SMP-01/05 JAN 2005 | Fifth issue |
| 6 | SMPS Based Power Plants | (No. : TEC/GR/FLA/SMP- 001/06/June.2010) | Sixth issue: Clauses pertaining to surge protection devices for protecting the telecom site, have been separated from the GR. Changes in few parameters have been incorporated to accommodate advancement. All cases for certification shall be treated as fresh cases, and no incremental tests are recommended for renewal of type approval |

REFERENCES

| 1. | QM-115 | Quality standard for calculation/verification of MTBF |
| --- | --- | --- |
| 2. | QM-118 | Quality reliability in product design. |
| 3. | QM-202 | Pictorial guidelines for Visual assessment of quality of printed board assemblies (PBA) & discrete terminal assemblies. |
| 4. | QM-204 | Guidelines for workmanship standards for repair & modification of printed wiring board assemblies. |
| 5. | QM-205 | Guidelines for standard of workmanship for printed boards. |
| 6. | QM-206 | Guidelines for standard of workmanship for printed boards assemblies |
| 7. | QM-207 | Guidelines for soft solder and fluxes for Telecom Equipments. |
| 8. | QM 210 | Guidelines for standard of workmanship for surface Mounting Devices. |
| 9. | QM-333 | Specification for Environmental Testing of Electronic Equipments for Transmission and Switching use. |
| 10. | ITUT Rec. O.41 | Psophomeric noise requirements. |
| 11. | IS: 5 | Standard on colours & shades. |
| 12. | IS: 101 | Methods of Sampling & Test for Paints, Varnishes & Related Products. |
| 13. | IS: 168 | Ready Mixed Paint, Air Drying, For General Purpose-Specification |
| 14. | IS: 613 | Standard on Bus-bars |
| 15. | IS: 1248 | Standard on Shunts. |
| 16. | IS: 1359 | Specification for Tinning requirements. |
| 17. | IS: 1554 with Amend. -1 (June 1994) | Standard for Cables & Wires. |
| 18. | ISO-9001-2000 | Quality Management Systems Requirements. |
| 19. | EN 61643 - 11 / A11 | Low Voltage Surge Protective Device – Part 11: Surge Protective Device connected to low voltage power system – Requirement and Tests |
| 20. | IEC 62305 - 1 | Protection Against Lightening – Part 1: General Principle |
| 21. | IEC 62305 - 2 | Protection Against Lightening – Part 2: Risk Management |
| 22. | IEC 62305 - 3 | Protection against lightning – Part 3: Physical damage to structures and life hazard |
| 23. | IEC 62305 - 4 | Protection Against Lightening – Part 4: Electrical & Electronic System Within Structure |
| 24. | IEC 60364 - 5 - 53 | Electrical Installation Of Building – Part 5 - 53: Selection & Erection of Electrical Equipments |
| 25. | IEC 61643- 1 (Second Edition 2005 – 03) | Low-voltage surge protective devices – Part 1: Surge protective devices connected to low-voltage power distribution systems – Requirements and tests |
| 26. | IEC 60364-5-53: 2001 Amendment-1 2002 – 04 | Electrical installations of buildings - Part 5-53: Selection and erection of electrical equipment - Isolation, switching and control |

PART 1

TECHNICAL REQUIREMENTS

No. : BSNL/Specification/SMP – 001/01/March.2014

1.0	Scope

1.1	This document contains the generic  requirements  of   Power Plants, based on High Frequency Switch Mode Techniques, using switching frequencies  of 20KHz and above, for the use  in  Indian Telecom Network. The Power Plant as per this GR shall be compatible with either VRLA or both VRLA as well as Conventional Lead Acid batteries. The power plant compatible with VRLA batteries only shall be certified as "SMPS power plants compatible with VRLA battery only". The Tendering Authority will indicate the type of power plant required in the Tender.

1.1.1		The DC Distribution cabinet does not form part of this GR.

1.1.2		The system shall be capable of meeting the load requirements of various telecom equipment and battery bank in Telecom Network. The system should be expandable at rack level itself or by additional racks using the basic FR/FC and/ or FR/BC modules of the same rating. The prescribed FR/FC and FR/BC ratings are 25A, 50A, 100A and 200A. These power plants may be mainly classified in two categories:

1.1.2.1		Large capacity Power plants systems:

These types of power plants are envisage for large or very large telecom systems. Power plant systems with ultimate capacity of 600A/1000A/1500A and above are envisaged for this application. Battery back-up for these systems shall be as per Annexure – I letter No. 7-1/2013-NWO-CFA/MSE (Ch.II) Dated: 14.03.2014 Issued by BSNL C.O, New Delhi – 110 001.   SMPS power plants based on 100A basic modules are envisaged for 600A/1000A/1500A and 100A/200A basic modules for above 1500A for these application. All these power plants use three phase supply.

1.1.2.2       	Small capacity Power plants systems:

These type of power plants are envisage to serve small telecom systems in rural and semi-urban areas. Battery back-up for these systems shall be as per  Annexure – I letter No. 7-1/2013-NWO-CFA/MSE (Ch.II) Dated: 14.03.2014 Issued by BSNL C.O, New Delhi – 110 001. This type of power plant may also be used with small telecom systems such as mobile base stations etc. in the urban and  metros areas. SMPS power plants with ultimate capacity of less than 150A (single phase) based on 25A/50A single phase module are envisaged and these power plants shall operate on single or three phase / 4 wire A.C input power distribution.

The power plants with ultimate capacity 150A/300A/450A based on 50A basic modules shall operate on three phase / 4 wire A.C input power distribution. Higher rated modules in place of 50A basic modules (60A/75A) is also permissible, but counting of modules will be as per the ultimate capacity fixed for 50A basic module (i.e 150A/300A/450A).

1.1.3		The    power   plant   system   shall consist of a Distribution, Switching, Control, Alarm and Monitoring arrangement (DSCA) and Float Rectifier-cum-Float Chargers (FR/FCs) and Float Rectifier-cum-Battery Chargers (FR/BCs) in a rack.  It shall employ modular configuration for flexible provision of DC power.

Note:    FR/BC is only used for conventional flooded Lead Acid batteries only. Power plants compatible with VRLA batteries only, do not require FR/BC modules and as such only FR/FC are used in such power plants.

1.1.4		The system   shall   be sufficiently flexible to serve any load from 6.25A onwards, depending on manufacturer's design, rating, number of FR/FC modules used in a rack and system configuration.

1.1.5	To cater to higher load requirements, same type of FR/FCs mounted in the same rack or different racks shall be capable of working in parallel load sharing arrangement.

1.2               		Functional and Technical Requirements

1.2.1		Functional Requirements

1.2.1.1		Lightning & Surge Protection:

The protection of Telecom Site against the lightening and high voltage surges shall be as per GR of Lightening and Surge Protection of Telecom Site (GR No. TEC/GR/FLA/LSP-001/01/June 2010).

1.2.1.2    		Stage–2 Protection:

This protection against, low voltage surges of up to 1.5 KV, shall be provided at the power plant level. This protection shall be equipped with thermal disconnection and potential free contact for arrestor(s) connected between live & neutral and neutral & earth. This protection shall be in compliance of IEC 62305 & 60364-5-53 for the following values of current:

| Between | Protection Requirement |
| --- | --- |
| R, Y, B & N | Greater than or equal to In: 10KA, 8/20S for each phase |
| N & PE | Greater than or equal to In: 20KA, 8/20S. |

Where In: Value of nominal discharge current 8/20S.

Note:  Voltage rating of MOVs shall be 320V minimum.

1.2.1.3     		Response time of the Stage II device shall be ≤ 25 nano seconds.

1.2.1.4	Installation procedures of SPDs

The power plant shall contain Stage-II protective device for protection against low voltage surges of voltage up to 1.5 KV.

1.2.2		Technical Requirements

1.2.2.1         		System Applications

SMPS is intended to be used in Auto Float-cum-Charge mode as a regulated D.C. Power Source.

1.2.2.1.1        	Switching frequencies of these power plants shall be 20 KHz and above.

1.2.2.1.2    	 	The system shall   only   be   based   on   menu   driven Microprocessor Controlled Techniques (both DSCA as well as FR/FC, FR/BC module) for control, monitoring & alarms. DSCA shall display the Software version and checksum number for DSCA and FR/FC, FR/BC. Setting of all the parameters shall be through menu-driven microprocessor control only. The failure of Micro processor or DSCA shall not affect the setting of individual FR/FC, FR/BC. No parameter of FR/FC, FR/BC modules shall be disturbed on the failure of DSCA. In this condition all the FR/FC FR/BC modules shall take care of the load on default settings and share the load collectively.  Only the setting of new parameters from DSCA shall be affected. In case of failure of microprocessor of FR/FC, FR/BC module its last settings shall not be affected.

The system shall be RS485 / RS232/ Ethernet compatible, if remote monitoring is required. It shall be feasible to set any monitoring control parameter from a remote site through RS 485.  All the information regarding Control and monitoring of Power Plant data shall be accessible on demand from the remote site. The exchange of information and protocol format shall be as given in the Annexure -1.

1.2.2.2      	The DSCA shall be provided for the ultimate capacity of the Power Plant. However, it shall preferably be provided either in the first rack or in a separate rack. The DSCA, in addition to control, monitoring and alarms, shall provide for the following:

a)  Termination for the batteries*.

b)  Termination for the exchange load.

c)  Interconnecting arrangement for power equipment.

d)  Battery Switching arrangement (Connection to / isolation from system)**

e) Termination for AC input to the rack shall be finger touch proof, flame retardant, insulated.  Use of bus-bars for the purpose is precluded. However, for terminating cables of large cross sectional area, especially in high ultimate capacity power plants, copper bars may be provided as terminal blocks to handle such high currents.

f)   Termination for AC and DC to FR/FC modules.

g)  Circuit Breakers/ fuses etc.

* The capacity and number of batteries shall be as per order. For  the  purpose of Type Approval, it shall be taken as three batteries.

** Only CACT approved DC contactor or `MCBs’ (which do not produce spark while cutting in or out)   for manual isolation and reconnection of the battery.  The manual isolation/reconnection of the battery by tripping the contactor through an external switch is not permitted.

Note-1:  For AC input supply, AC contactor with AC Coil shall preferably be used.  AC Contactor with DC coil (if used) shall have its own power supply and shall not be fed from Exchange battery.

Note-2: Battery shall be protected against the short circuit from any source, including switching equipment such as contactor, MCB coil and their control  and sensing circuitry.

Note-3:  Solid state switching   device may preferably be used. Relays, if used, shall be UL or CE compliant.

1.2.2.2.1      	Interlocking   of batteries: Necessary interlocking arrangement for batteries shall be provided so as to ensure that at-least one battery remains floated across the load under all working conditions.

1.2.2.3	Power Plant compatibility with Engine alternator:  The power plant system (including FR/FCs, FR/BCs and DSCA), shall be suitable for operation from A.C mains or a DG set (of capacity 1.25 times AC load of power plant).

1.2.2.4	Load Sharing (Parallel operation): FR/FC modules shall be suitable for operating in parallel with one or more modules of similar type, make and rating,   other output conditions remaining within specified limits.

1.2.2.4.1       	The current sharing shall be within +/- 10% of the average current per rectifier module in the system (mounted in the same or different racks), when  loaded between 50 to 100% of its rated  capacity for all  working  conditions.

1.2.2.4.2       	In the   event of failure of DSCA, FR/FC, FR/BC  modules’ parameters shall not be disturbed.  All the FR/FC FR/BC modules shall take care of the load on default settings and share the load collectively.

1.2.2.5           	Battery Monitoring:

1.2.2.5.1    	Battery under voltage isolation:   There shall be a   provision   for Automatic isolation/reconnection of each battery from the load. The DC contactor used for the purpose shall be of single pole only.

The operate and release voltages for the above conditions shall be as follows:

Cut-off: 1.85V/cell (44.4V+0.25V) shall be settable between 1.85V and 1.9V/cell)

Reconnect: When the FR/FC voltage has built-up fully. Shall be settable between 2.15V to 2.3V/cell)

1.2.2.5.2      	Battery   Health   Monitoring in Auto Mode:    To keep the battery in healthy state, the battery condition shall be continuously   monitored.  On restoration of AC mains after an interruption, depending on the sensed battery condition (depth of discharge), the system shall change over to Auto Charge mode to charge the battery at higher voltage of 55.2V till the battery is fully recouped.

1.2.2.5.3       	Battery Health Check (Optional):   There   shall be a provision of monitoring the voltage, current, trickle current, conductance and temperature (programmable) of the batteries associated with the power plant at a set periodicity. There shall also be a provision of monitoring of each cells of the battery bank for voltage and temperature.

The provision for conducting a partial discharge (about 20%) test, of a pre-determined duration and frequency, shall be made available in the power plant (Frequency and duration of partial discharge test shall be programmable). During this test, the current and voltage of the battery as well as each individual cell shall be recorded. It shall also   record the conductance and temperature of each cell.

Conductance measurements/observations shall be off-line to prevent noise interference. First observations of conductance, recorded by the power plant system, for the battery shall form the base values for future comparison.

The provision  of partial test discharge shall  be implemented  in such a way that at a time only one battery is put to discharge, so as to ensure that necessary battery reserve is available in case of power failure during or immediately after the test discharge. Provision shall be made for observing the state of charge of battery before commencing this test. In case the battery is not fully charged this test may be deferred till the battery is fully recouped.

Any abnormality observed during above observations shall be highlighted by initiating an alarm. All the above information shall be made available to the remote site through RS 485(Refer Annexure 1 for specified protocol).

Note: The Battery Health Check feature shall be optional.  However, type approval shall only be accorded with the above provision. The manufacturer will give the list of hardware equipment required for the purpose in the instruction and maintenance manual.  User shall clearly indicate the requirement of battery health check feature while ordering the power plant.  The manufacturer shall also undertake that the above provision will become fully function by adding the hard ware (indicated in the instruction manual) for the purpose.

1.2.2.5.4       	SMPS Management (Optional)

The purchaser may decide the requirements for optional SMPS Management features like Energy saving Management, DG Efficiency & Fuel Saving Management, Battery Efficiency & Management, Rectifier Control – Efficiency Management, etc.

1.2.2.5.5       	Battery  path  Current  Limiting  Circuit : In  Auto Mode  the current in each battery path shall  be  settable   as  per  the battery capacity  so  that  the battery  path  current  is kept at 10 % of  battery  AH  capacity.  Tendering Authority will give the capacity of the battery to be used for this purpose. For the type approval the manufacturer shall demonstrate the facility and undertake to make provision as  per order.

1.2.2.5.6     	Temperature Compensation for Battery: In auto float/charge, mode there  shall be  provision for  monitoring  the  temperature  of  battery  and  consequent arrangement for   Automatic  temperature  compensation  of  the FR/FC, FR/BC output voltage to match  the  battery  temperature dependant charge characteristics. The output  voltage  of  the  rectifier  in Float/Charge operation shall  decrease  or  increase  at  the rate of 72mV (3mV/cell, 24  cell  battery)  per degree increase or decrease in temperature over the set  voltage. The output voltage shall decrease till the open circuit voltage of the battery is reached. The open circuit voltage range shall be settable between 2.1V/cell to 2.2V/cell. At this voltage, the power plant voltage gets locked and further increase in temperature shall not decrease the voltage any further. This voltage shall also remain locked till the temperature falls below the value corresponding to set value. When the output voltage reaches 55.8V, due to increase in the output voltage owing to decrease in temperature, it shall get locked at this voltage & any further decrease in temperature shall not lead to further rise in the output voltage of the power plant. This voltage shall also remain locked till the temperature rises above the value corresponding to set value.  A tolerance +/- 5 mV may be acceptable over the specified rate of 72mV/degree C. The nominal distance between the battery & power plant may be 20 metres. The manufacturer shall provide the necessary sensor and cord for the purpose with the power plant.  Failure of temperature   compensation circuit including sensors (including the open or short circuit) shall create an alarm and shall not lead to abnormal change in output voltage.  Proper sign-writing shall be made in DSCA and both ends of temperature compensation cord for its easy termination.

1.2.2.6        	Protections

Failure   of   control and sensing circuitry shall not cause any hazard. The voltages of the system shall not abnormally increase to endanger the load.

1.2.2.6.1     	AC Input:   There   shall   be an automatic arrangement to provide galvanic isolation at the AC input of the FR/FC module whenever the input voltage is beyond the specified operating range (90V to 300V for single phase and 320V to 480V for three phase systems). Suitable alarm indication shall also be provided. The FR/FC module shall resume normal working automatically when the input is restored within the working limits. Hysteresis within specified working limits shall   prevent shutting down of the FR/FC. A tolerance of      +/- 5V is acceptable for protection & alarm operation. Reconnection shall occur at a voltage, 10V lower than the set voltage for high isolation limit and 10V higher than the lower set limit, to avoid hunting. The circuitry used for sensing the voltage for operation of isolation/ reconnection device shall be able to withstand a voltage 15% higher than the specified extreme limit of isolation.

1.2.2.6.1.1   	The module shall be isolated (if required for the protection of the unit) in the   event of unbalance beyond 10% and shall restore when the input is within limits.

1.2.2.6.2       	D. C. Over voltage:  Each rectifier module shall be fitted with an internal over- voltage protection circuit.

1.2.2.6.2.1	In case output DC voltage exceeds –56V, the over voltage protection circuit  shall  operate and shut-off the  faulty  module.  A tolerance of +/-0.25V is permitted in this case. Restoration of the   module may be through manual or through DSCA”.

1.2.2.6.2.2   	Shutting-off of faulty FR/FC module shall not affect  the operation of other FR/FCs operating in the rack.

1.2.2.6.2.3    	Operation of over-voltage shut down shall be suitably indicated on the module and also extended monitoring/control unit.

1.2.2.6.2.4    	The   circuit design shall ensure protection against the discharge of the Battery through the FR/FC module in any case.

1.2.2.6.2.5      	The over voltage protection circuit failure shall not cause any safety hazard.

1.2.2.6.3       	Fuse / Circuit Breakers:  Fuses or circuit breakers shall be provided for each FR/FC, FR/BC module as follows:

a.	Live AC input line (MCB)

b. 	Negative D.C output (enclosed ultra-fast blow fuse assembly or DC circuit-breaker).

c. 	Against failure of Control sensing circuit.

1.2.2.6.3.1      	All fuses/circuit breaker used shall be suitably fault rated.

1.2.2.6.4     	Over Load/Short Circuit:  The FR/FC shall be protected for over load/short circuit as per clause 1.2.2.10.9.2.

1.2.2.7         	Monitoring Alarms and Indicating Lamps

Visual    indications/display shall be provided by means of bright LCDs/LEDs on each FR/FC module and DSCA to indicate:

1.2.2.7.1       	Functional Indications:  The following functional indications shall be provided on FR/FC & DSCA :

a) Mains available

b) FR/FC, FR/BC On Auto Float

c) FR/FC, FR/BC On Auto Charge

Note: The functional indication a) shall be provided on both DSCA & FR/FC/BC module, while   b) & c) may be provided either on DSCA or on both FR/FC and DSCA.

1.2.2.7.2       	Alarm Indications:

A.  On FR/FC:

a. LED Green – Healthy

b. LED Amber – Warning

c. LED Red – Major

B.   On DSCA:

a)   Load Voltage High (above 56V)/Low (below 45.6V)

b)   FR/FC, FR/BC fail due to:

i). FR/FC, FR/BC Over Voltage

ii). FR/FC, FR/BC Under Voltage or Output fail

iii). FR/FC, FR/BC Over Load (Voltage droop)

iv). Fan Fail (due to any reason).

c)   Mains Out of range

d)  System Over Load

e)   Mains "ON"/Battery Discharge

f)   Fan Fail (in case fan provided at rack level)

g)   Temp. Compensation fail

h)   Battery Fail or No Battery (separate for each Battery)

i)   Battery isolated from the load

j)   Lightning and surge protection Stage II Fail

1.2.2.7.3	All the alarms shall be DC operated only. Also all alarm circuits shall be provided with suitable delay to ensure that they do not operate with transients.

1.2.2.7.4     	All the alarms and protection limits shall be settable through a menu driven program.

1.2.2.7.5       	All the protections/alarms shall be within tolerance of 0.25V in   case of DC voltage and 1% in case of current. For AC voltage it shall be +/- 5V.

1.2.2.7.6        	Every Alarm condition shall be accompanied with an Audio alarm, with audio cut-off facility.

1.2.2.7.7       	Potential free contact two (one for alarm and one redundant) shall be provided for extending the fault alarm to Switch room.

1.2.2.8       	Remote control and monitoring

The power plant shall be RS 485 compatible. It shall provide for the monitoring, alarm and control of the power plant and its associated batteries from a remote site through RS 485.   The exchange of information and protocol format between the power plant and remote site shall be as given in the Annexure-1.

1.2.2.9          	Electrical Requirements

1.2.2.9.1      	AC  input  Supply : The  Power  Plant  using  FR/FC modules of 50A shall  operate  from  single  phase AC input & FR/FC module of 100A capacity shall operate from three phase/4 wire AC input. The nominal input frequency is 50Hz, which may vary from 48-52Hz. The input voltage range shall be as given below:

a) Single Phase (Nominal 230V)	:  120V to 300V

b) Three Phase/4 wire (Nominal 400V)	:  320V to 480V

50A FR/FC module shall operate on single phase with three phase / 4wire AC input distribution. Power Plant shall cut off below 120V.

1.2.2.9.1.1   	For three phase/4 wire FR/FC, FR/BC modules only delta connections are permitted.  FR/FC, FR/BC modules shall work   satisfactorily for unbalance of  +/- 10% of nominal input.  Phase current unbalance, under all working conditions, mentioned in this document, shall not be more than 10%. Neutral phase current shall not exceed 100mA under all specified input and load conditions.

1.2.2.9.1.2         Power Derating:

- Power de-rating for Single Phase FR/FC Modules: Power plant shall deliver 60% of rated capacity for input operating range of 120 to 185V and 100% of rated capacity for input operating range of 185 to 300V. Power Plant shall cut off below 120V.

- Power de-rating in case of SMPS power plant operating on three phase with 100A FR/FC Module, shall be able to operate on two phase with output power de-rating of at least 50%.

1.2.2.9.1.3         Neutral path  current in case of single phase FR/FC modules in each phase of three phase distribution shall not exceed the limit set by State Electricity Board / Other Regulatory Authority.

1.2.2.9.2     	DC output Characteristics (Auto Float Charge operation):  The Module shall be capable of operating in “Auto Float-cum- Charge” mode. It shall be programmed to operate as a float rectifier or a charger, depending on the condition of the battery sets being sensed by the DSCA.

1.2.2.9.2.1    	Auto Float Mode: The float voltage of each rectifier module shall be continuously adjustable and pre-settable at any value in the range of -48 to -56V from FR/FC, FR/BC modules or DSCA.  There shall also be a provision of setting the float/charge voltages globally from DSCA. There shall also be a provision so that DSCA may over ride the values set by individual module. The prescribed float voltage settings are -52.8V for conventional battery and -54V for VRLA battery respectively. Float Voltage adjustment may be made globally, and not for individual rectifiers”.

1.2.2.9.2.2   	Auto Charge Mode: In Auto charge mode FR/FC  shall  supply  battery  & equipment current till terminal voltage reaches set  value,  which  is normally  2.3V/cell (-55.2V, this value shall be settable between -48V and -56V) and  shall change over  to  constant   voltage  mode. It shall remain in this mode till a change over to   float mode signal is received.

1.2.2.9.2.3   	The DC output voltage at the terminals shall be maintained within +/-1% of the half load preset voltage from 25% load to full load condition when measured     over the full specified input range.

1.2.2.9.3      	Efficiency: The efficiency of the single phase and three phase unit shall be as given below:

Single Phase AC    Three Phase AC

a) At nominal input, output and full rated load 	   better than 89%       better than 90%

b) Other specified Input, output conditions 	better than 85%      better than 87%

and load between 50% to 100%.

1.2.2.9.4      	Input Power Factor: The true input   Power Factor at nominal   input, output voltage and rated load shall be better than 0.98 and shall be better than 0.95 in any other working condition and load between 50% to 100%. Active Power factor correction only shall be employed for the purpose.

1.2.2.9.5   	A resistor shall be provided to discharge the capacitors after the Rectifier modules have stopped operation and output is isolated.

1.2.2.9.6     	Electrical Noise: The Rectifier (FR/FC) Modules shall be provided with suitable filter on the output side.

1.2.2.9.6.1    	Psophometeric Noise:  Psophometeric Noise (e.m.f.  weighted  at  800Hz),  with  a   battery  of appropriate capacity connected across the output should  be within  2mV,  while delivering the full rated load  at  nominal  input (400V AC for  three phase supplies and 230V for single phase supply).   For   test purposes, this shall be taken as equivalent to 4mV when the battery is not connected, other conditions remaining the same as per ITU-T Rec. O.41.

1.2.2.9.6.2  	The Peak-to-Peak  Ripple : Voltage at  the output  of  the rectifier module, without battery connected, shall not exceed 300 mV  at the  Switching  Frequency  measured by an Oscilloscope  of  50/60  MHz   band-width (Typical).

1.2.2.9.7       	Transient Response

1.2.2.9.7.1  	Soft Start Feature:  Slow start circuitry shall be employed such that FR/FC module input current and output voltage shall reach their nominal value within 10 seconds.  The maximum instantaneous current during start up   shall not exceed the peak value of the rectifier input current at full load for the lowest input voltage specified.

1.2.2.9.7.2   	Voltage overshoot/Undershoot   :   The    requirements    of    this clause    shall     be achieved without a battery connected to the output of FR/FC module.    The FR/FC modules shall be designed to minimise output  voltage Overshoot/ Undershoot such that when they are switched on the DC output  voltage shall be limited to +/-5% of the set voltage & return to their steady state within 20 ms for any load of 25% to 100%.

1.2.2.9.7.3  	The DC output voltage overshoot for a sudden change in AC  mains from specified lowest to highest and vice-versa shall not cause shut- down of FR/FC module  and  the  voltage  overshoot shall be limited to +/-  5%  of  its  set  voltage and return to steady state within 20 ms.

1.2.2.9.7.4   	The modules shall be designed such that a sudden  load change of 25 to 100% shall not result  in  DC output  voltage Overshoot/ Undershoot of  not  more  than 5%  and  return to steady state value within 10 ms  without resulting the unit to trip.

1.2.2.9.8      	Total Harmonic Distortion

1.2.2.9.8.1  	Total Voltage Harmonic Distortion:  The Total line harmonic voltage   distortion shall not be more than 10% in conformity with CIGRE's limits.

Note: The above Harmonic Distortion limits are as per  communication received from Central Electricity Authority vide their office  letter No. GO2/Comm.I/1/1-95/962 dated 22.12.92.

1.2.2.9.8.2  	Total Current Harmonic Distortion: The total harmonic distortion shall be limited as per EN 61000-3-2 Ed.2:2000. The total current  harmonic distortion  contributed by the unit at the input shall not exceed  10%  for  input voltage range 90V-300V for single phase units and 320V  to 480V for three phase  systems; for load  between 50 to 100% of the rated capacity.

1.2.2.9.9      	Current limiting (Voltage Droop):    The Current limiting (Voltage Droop) shall be provided for Float/Charge operation.  The float/charge current limiting shall be continuously adjustable between 50 to 100% of rated output current for output voltage range of -44.4 to -56 volts. For test purposes upper limit of 100% + 5% and lower limit of 50% - 5% shall be acceptable.

1.2.2.9.9.1   	The float and charge current limit adjustment shall be provided:

Either on the front panel of the individual FR/FC, FR/BC module through a menu driven program

or

Through a provision at the centralised location on front panel of DSCA through a menu driven program capable of adjusting the float and charge current limits of the each FR/FC, FR/BC module individually, irrespective of the rating and number of modules located in the same rack or in other racks of the power plant for the ultimate capacity of the system.

1.2.2.9.9.2   	The FR/FC modules shall be  fully  protected  against  short  circuit. It shall be ensured that short circuit does not lead to  any   fire hazard. The unit shall start delivering output automatically when the short circuit is removed.

1.2.3              	Power Plants Compatible with Conventional Batteries

1.2.3.1         	The conventional  lead  acid  batteries  have special requirement  of  periodic  Boost charging @ 2.7V/cell.  To meet  this requirement,  the power plant shall be so configured that in  addition  to the specification requirements, detailed in clause 1.1 to  2.2.9.3,   shall  also  have  a  provision of a group  of  FR/BC(as  per  battery  capacity)  for charging the batteries (one set at a time)  @  2.7V/cell  after isolating both the battery and FR/BC group from the load bus. In  addition to FR/FCs the power plant shall have the following additional  units.

1.2.3.2      	Float Rectifier-Float Charger-Boost charger (FR/BC) :  The FR/BC module shall be programmable to work as FR/FC or BC.

1.2.3.2.1        	When programmed, FR/FC it shall be capable of working as  FR/FC  with other FR/FC and shall comply with all the requirements of  FR/FC. The rated capacity of the FR/BC as FR/FC shall be same as that of  the  other  FR/FCs. The prescribed Float voltage setting  for  conventional  batteries is 52.8V.

1.2.3.2.2        	It  shall  also  be  programmable  as  a  Boost  Charger  (BC)  under   manual control after isolating it from the float bus.

1.2.3.2.2.1     	As a Boost charger its output voltage shall be continuously   adjustable and pre-settable at constant current up to 100% for voltage range 44.4V to 56V and up to 50% of the rated capacity at any value in   the range 56V to 64.8V.

1.2.3.2.2.2     	The   Boost   voltage shall be maintained within +/-1% of the set value over the full boost current range as specified in clause.

1.2.3.2.2.3     	The  Float   and  Boost current  limit  adjustment  shall  be provided on the front panel of the FR/BC module.

1.2.3.2.3     	Parallel operation in BC mode: When programmed in BC mode FR/BC modules shall be working in parallel load sharing arrangement with other FR/BC modules in the same mode, other output conditions remaining within specified limits.

1.2.3.2.3.1     	The current  sharing  shall be within +/- 10%  of the  average current per FR/BC module (in BC mode) in the system (mounted in the same  or  different  racks)  when  loaded  between  50  to 100% of its rated  capacity (as BC) for all other working conditions.

1.2.3.2.4      	In addition to the Visual indications/display specified for FR/FC the following shall also be provided:

Functional Indications: FR/BC on Boost mode

Alarm Indications: Following Alarms shall actuate in BC mode:

a. FR/BC over voltage

b. FR/BC Over Load (Voltage Droop)

1.2.3.2.5      	Protection:    The   module   shall also be protected against D. C. Over voltage in BC mode.

1.2.3.2.5.1   	Shutting-off of faulty FR/BC module in FR/FC mode shall not affect the operations of other FR/FC & FR/BC in FR/FC mode and  other  BC while working in BC mode.

1.2.3.3        	Distribution,  Switching,  Control,  Alarm  and   Monitoring Unit:  The Distribution/ switching/ Control  and  alarm  unit, in  addition  to  the  facilities  specified earlier  shall also provide for :

1.2.3.3.1     	Switching   Arrangement:   The   switching    arrangement    may have handled enclosed knife fuse assembly or any other suitable arrangement in the same or separate rack for the following facilities:

a)  FR/BCs in Auto Float

b) Selection and switching a Group of FR/BC for Boost or Float Charge operation.

To achieve the above the switching arrangement shall be capable of selecting:

1.2.3.3.1.1      	Battery Auto Float Charge/Boost selection arrangement for selecting:

i) All the batteries in Auto Float Charge Mode

ii) Battery-1 on Boost others on Auto Float Charge.

iii) Battery-n on Boost others on Auto Float Charge

1.2.3.3.1.1.1  	The above arrangement shall be provided with a suitable inter-locking arrangement so that one of the batteries is always on   Float.  In case interlocking arrangement is not feasible due to the rack size, a provision of Alarm shall be made in the event of all the batteries are isolated accidentally.

1.2.3.3.1.1.2 	The capacity and number of batteries shall be as per order. For the purpose of Type Approval, it shall be taken as three batteries.

1.2.3.3.1.2   	FR/BC switching arrangement:  This switching arrangement shall   be provided for connection of FR/BC group to the Float bus for Auto Float Charge operation or Boost Charge bus for Boost Charging of the battery after its isolation from the Float Bus.

1.2.3.3.2     	Alarms:   The following   additional alarms   shall be provided for Boost Charge operation FR/BCs.

Functional Indications:  FR/BCs in Boost Charge Mode

Alarm Indication:

a) Boost Load Voltage High (above 66V)/Low (below 44.4V)

1.2.3.4          Sleep Mode Operation: While calculating the composition of a particular power plant, the power plant ultimate capacity/SMPS module rating, the sum total of the load current and charging current of the battery is considered. In actual operation the battery is fully charged, the power plant will supply to only exchange load. Under this condition keeping all the modules “ON” will result in poor over all efficiency. Hence by selecting to switch off the extra modules will improve the overall power consumption and also result in higher reliability and life time of the modules. This is feature is popularly known as “SLEEP MODE”.

- PART 2

- GENERAL REQUIREMENTS

No. : BSNL/Specification/SMP – 001/01/March.2014

2.0                 	General Requirements

2.1                	Radio  Frequency Interference (RFI) Suppression : The system (FR/FC,   FR/BC &  DSCA  modules)   shall  be  designed  to  minimise  the  level    of electromagnetic interference (EMI), both conducted and radiated, detected in its vicinity and generated by the module  and  shall comply the following clauses :

2.1.1           	Radiated   Emission   from   the   single phase and   three phase Power equipment.

Requirement: Any network of conductors & apparatus connected thereto shall not exceed the level of field strength specified in IEC-CISPR 22 ‘A’ as given below:

| Frequency (F) [MHz] | Distance (Meters) | Quasi peak limits dB(V/m.) |
| --- | --- | --- |
| 30 - 230 230 – 1000 | 10 M 10 M | 40 dB(V/m). 47 dB(V/m). |
| 1. The lower limit shall apply at the transition frequency. 2. Additional provisions may be required for cases where interference occur |  |  |

Test Procedure: Test setup, Test procedure & Measurements shall be conducted as per IEC- CISPR 22.

2.1.2            	Conducted   Emission Limits    :   All   conducted    emissions    from    power equipment or accessories connected thereto, intended to be connected to the power lines of a public utility shall not exceed the limits specified in IEC- CISPR 22 ‘A’ as given below :

| Frequency (MHz) | Quasi peak limit dB(V) | Average limit dB(V) |
| --- | --- | --- |
| 0.15 - 0.5 0.5 - 30.0 | 79 dB(V) 73 dB(V) | 66 dB(V) 60 dB(V) |
| The lower limit shall apply at the transition frequency |  |  |

Test Procedure: Test set up, Test procedure & Measurements shall be conducted as per IEC - CISPR 22.

2.1.3            	Conducted   Susceptibility Limits     :   Power equipment used in Telecom Network shall not malfunction when high voltage surge as specified below is superimposed at the input power mains to the power equipment, for more than two seconds as per IEC 61000- 4-12, 9(b). The equipment shall also not fail or degrade in performance after the surge is withdrawn.

Test levels:

Voltage Rise time (First peak)	: 75 nano sec +/- 20%.

Oscillation Frequencies	: 100KHz & 1 MHz +/- 10%

Repetition rate                      	: at least 40/s for 100KHz and 400/s for 1 MHz

Decaying               		: 50% of the  peak value between the 3rd & 6th periods

Burst duration                   	: not less than 2 s

Surge amplitude              	: 250V(-10% ) to 2.5 KV(+10%)

Wave shape                     	: Damped

Test Procedure:  Test set up, test procedure & Measurements shall be as per IEC 61000-4-12. EMI surge of specified levels injected on power leads of test sample shall not cause degradation of performance or malfunction

2.1.4            	Electrostatic    discharge (ESD) immunity limits: The limits shall be as per IEC 61000- 4-2, 9(1) (both Contact discharge method and Air discharge method) as given below:

Test level:

| Contact discharge |  | Air discharge |  |
| --- | --- | --- | --- |
| Level | Test voltage KV | Level | Test voltage KV |
| 4 | 8 | 4 | 15 |

Test Procedure: This test shall be conducted as per IEC 61000-4-2 for both requirements & unit shall comply of clause 9(1) of IEC 61000-4-2

2.1.5              	Electrical   fast transient/Burst    immunity limits:  The limits shall be  as specified in  IEC 61000-4-4.

Test level:

| Open–circuit output test voltage (+/-10%) &repetition rate of impulses (+/-20%) |  |  |
| --- | --- | --- |
| Level | On Power supply port, Protection Earth |  |
|  | Voltage peak KV | Repetition rate KHz |
| 4 | 4 | 2.5 |
| Rise time of one Pulse - 5 ns +/- 30% Impulse duration - 50 ns +/- 30% |  |  |

Test Procedure: This test shall be conducted as per IEC 61000-4-4. Test results shall be in compliance of clause 9(1) of IEC 61000-4-4

2.1.6           	Radiated radio-frequency    Electromagnetic   field immunity limits: The limits as per IEC 61000-4-3.

Test level:

| Frequency range : 80 MHz to 1000 MHz. |  |
| --- | --- |
| Level | Test field strength V/m |
| 3 | 10 |

Test Procedure: This test shall be conducted as per IEC 61000-4-3. Test results shall be in compliance of clause 9(a) of IEC 61000-4-3.

2.1.7              	Surge immunity limits: The limits as per IEC 61000-4-5.

Test level:

| Level | Open circuit test voltage( +/- 10% ) KV |
| --- | --- |
| 1 2 3 4 | 0.5 1.0 2.0 4.0 |
| Voltage surge - 1.2/50 s Amplitude - 2 KV(DM) - 4 KV(CM) - After testing for 4KV, the amplitude shall also be increased to 6 KV (1.2/50 s) Combined wave form as per IEEE C62.41- 1991 to cover Lightening/ Surge protection test also. - Test results shall be in compliance of clause 9(b) of IEC 61000-4-5. |  |

Test Procedure: This test shall be conducted as per IEC 61000-4-5.  After testing for 4KV, the amplitude shall  also   be increased to  6 KV (1.2/50 s) Combined wave form as per IEEE C62.41-1991(to cover Lightening/ Surge protection test also).

Note: The rated voltage of the MOVs used for the above shall not be less than 320V.

2.1.8            	Radio-Frequency Conducted Susceptibility immunity limits : The limits  as per IEC 61000-4-6.

Test level:

| Frequency range : 150 KHz- 80 MHz |  |
| --- | --- |
| Level | Voltage level ( e.m.f.) |
| 3 | 10 |

Test Procedure:  This test shall be conducted as per IEC 61000-4-6. Test results shall be in compliance of clause 9(a) of IEC 61000-4-6

2.1.9             	At the   Time of Type approval the testing officer shall ensure that the power plant is in compliance of the clauses 2.1.1 to 2.1.8 given above.

2.2                 	Power Plant System Configuration:

2.2.1             	The   system shall employ a modular configuration to provide flexibility, keeping in view the future load requirements of D.C. Power.

2.2.2          	The FR/FC, FR/BC modules shall be accommodated in a rack. DSCA, for the ultimate capacity,   shall be provided in first rack or in a separate rack as per manufacturer's design. AC and DC distribution may, however, be provided in First/separate rack or in the individual racks. In case, distribution arrangement is provided in First/separate rack, it shall be for the ultimate   system capacity.   In  case  the   Distribution  is provided  in  the individual  racks  DC  distribution/switching shall be for the ultimate  system  capacity,  while  AC distribution shall be for fully  equipped rack. All factory wiring for the rack shall be for the ultimate capacity so that only plugging-in of FR/FC or FR/BC module shall enhance the DC power output.

2.2.3             	The requirement for Single Rack & Auxiliary Rack will be defined by purchaser, depending upon the requirements and ultimate capacity of power plant.

2.3               	Rack Configuration:   Rack is composed of following units, accommodated in 19" (482.6 mm) Sub-rack:

a)  Float Rectifier-cum-Float Charger (FR/FC) and/or Float Rectifier-cum-Battery Charger modules ( FR/BC).

b)   Distribution, Switching, Control, Alarm and Monitoring (DSCA) unit.

2.4                 	Constructional features:

2.4.1     	Rack: The   rack   structure shall be made up of rigid frame work of steel profiles and shall be free of sharp edges or sharp corners. The  structural  strength  of  the  rack  shall  be  able  to  withstand  the  ultimate mechanical load capacity of the rack without any deformity. The rack shall have suitable ventilating arrangements (forced cooling from the sides is not permitted). The front door (if provided) and rear door may be of hinged or removable type.  The gauge of metal sheet for panels shall not be less than 2mm. The unit may be floor-mounted or wall-mounted as specified by the purchser. The unit may be either expandable or of ultimate size, as per purchaser’s requirement”.

2.4.1.1          	The   base  of  rack   shall  ensure  uniform  floor  loading  of  not   more  than  975 kg/Sq metre. Lifting  facilities shall  be  provided  by  removable  eyebolt  located  at the top of  the  rack.  The necessary arrangement for fixing the rack on the floor shall also be provided. The rack shall also be provided with bottom clearance of 110 mm with a tolerance of +/- 10mm.

2.4.1.2          	The top of the rack shall be fully covered except for proper   ventilation and bus bar or cable entries. Each air  flow vent shall be  covered  by  a  grill to  prevent foreign  material  larger  than  5 mm dropping into the rack.

2.4.1.3          	The rack shall be designed for easy maintenance and installation.  Rack mounting arrangement shall provide easy access   from front, rear and top for Installation and Maintenance.

2.4.1.4        	The   individual FR/FC module shall be easily mounted to/removed from the front side of the rack. The FR/FC module shall be designed to slide into the rack on a suitable mechanical arrangement. The associated AC input, DC output  connections, Control, alarms & interface cable connecting the modules shall be connected/disconnected easily  without  causing  any interruption in  the  supply  and  damage to load or other  working module.

2.4.1.5        	Proper  thermal  engineering  of  hardware  design  shall  be  done  by the manufacturer so as to ensure the uninterrupted use of the equipment. The rack  complete with  all panels  fitted shall be designed to allow cooling by natural  convection. For  the  systems, using 25A, 50A, 100A  & 200A FR/FC, FR/BC modules force cooling is permitted.  Use of DC Fans only are  permitted for the purpose. There shall be an arrangement   for  automatic  Switching-OFF  of fans  during  AC input failure. If  required, individual modules may be separated by air baffle to provide effective  convection. The manufacturer shall also ensure that the failure of fan does not cause any fire hazards. The failure of any of the fans shall draw immediate attention of the maintenance staff.

2.4.1.6          	Facility shall be made to connect external AC power  at  the  top/bottom of rack and alarm cable & DC output distribution module  at    the top of the rack. Where cables pass through metal panels   suitable   bushing shall be provided to protect cables from damage. Bus-bars,  if  used, shall be suitably spaced,  insulated and bushed(where it passes through holes) to prevent any possibility  of short circuit between bus-bar and/or rack.

2.4.1.7           With doors in position, all Visual alarms  &  meters   shall  be  clearly visible. In case of hinged door meters & alarm indications are permitted on door provided, the fixtures on the   door do not restrict the movement of door in any way.

2.4.1.8           	Dimensions: The rack shall only be 19” (482.6mm). Nominal dimensions of the rack may be as under:

| System Type | System capacity (Module Rating/Ultimate System Capacity) | Dimensions H (max.) X W (max.) X D (max.) |
| --- | --- | --- |
| For Small Power plants systems | 25A/150A (single phase) 50A/150A (single phase) 50A/300A (single phase) 50A/450A (single phase) | 1500mm X 750mm X 600mm |
| For Large Power plants systems | 100A/600A (Three phase) 100A/1000A (Three phase) 100A/1500A (Three phase) 200A/3000A (Three phase) 200A/4800A (Three phase) | 2200mm X 750mm X 600mm |

Note: Tendering authority shall clearly specify the height of the rack as per his power room/equipment room requirements.

2.4.1. 9          SMPS Power Plant System Ultimate Capacity:

(a) SMPS Power Plant with Single Phase 25A/50A FR/FC Modules with single phase A.C Supply.

(b) SMPS Power Plant with Single Phase 50A FR/FC Modules having three   phase distribution in to three ratings:

Power Plant categorized in to three ratings:

- Power Plant with Ultimate Capacity 150A (2+1) configuration              (with R/Y/B= 1+1+1), housed in a single rack.

- Power Plant with Ultimate Capacity 300A (5+1) configuration                 (with R/Y/B= 2+2+2), housed in a single rack.

iii. Power Plant with Ultimate Capacity 450A (8+1) configuration                     (with R/Y/B= 3+3+3), housed in a single rack.

Higher rated modules in place of 50A basic modules (60A/75A) is also permitted, but counting of modules will be as per the ultimate capacity fixed for 50A basic module (i.e 150A/300A/450A).

(c)  SMPS Power Plant with Three Phase 100A FR/FC Modules: Power Plant categorized in to three ratings:

- Power Plant with ultimate capacity 600A (in Single Rack)

- Power Plant with ultimate capacity 1000A (in Single Rack)

- Power Plant with ultimate capacity 1500A (can be in two Racks with

Main Rack capacity up to 1000A & Extension Rack capacity up to 500A).

(d) SMPS Power Plant with Three Phase 200A FR/FC Modules with capacity more than 1600A.

2.4.2              	FR/FC, FR/BC Module:

2.4.2.1          	The FR/FC, FR/BC modules   shall be cooled   by natural convection for smaller capacities i.e. 6.25A, 12.5A. FR/FC or FR/BC modules of 25A, 50A, 100A and 200A may have natural or forced cooling.

2.4.2.2       	AC input to FR/FC or FR/BC shall be through composite type hot plug-in connectors. DC output shall be through hot plug-in connector on the FR/FC or FR/BC side and through lugged termination on the bus-bar/termination end. Control, alarm and monitoring connections shall only be through polarised connectors.

2.4.2.3          	The FR/FC, FR/BC module shall be removable from the front of the rack only. All AC input, DC output and alarm/control/monitoring cables interconnecting the modules and racks shall be easily disconnected by plugs or connectors.

2.4.3              	Distribution, Switching, Control, Alarm and Monitoring (DSCA)

2.4.3.1        	The   Distribution/Switching   sub-system of DSCA   shall    preferably be modular but Control, alarm and monitoring sub-system shall only be modular. The Distribution/Switching sub- system may be accommodated in a rack with other FR/FCs, FR/BC or in a separate rack. These sub-systems shall be rack mountable.

2.4.3.2        	DSCA shall preferably be housed in the upper portion of the rack above the FR/FC or FR/BC modules.

2.4.3.3          	DSCA   shall   be   provided   for the ultimate system capacity as explained in Clauses 2.2.2 and 2.2.3.  All AC, DC or control/alarm cabling/wiring shall be pre-wired for   the ultimate capacity so that mere plugging-in of  FR/FC, FR/BC module shall add to the DC  power output. It shall be ensured that the modules are not site specific.

2.5                 	Accessibility

2.5.1              	All the termination points shall be easily accessible from front, rear or top.

2.5.2	AC and DC terminals shall be separated by physical barriers to   ensure safety.

2.5.3               All the terminals except AC earth shall be electrically isolated.

2.6                 	Terminations:

2.6.1              	AC Terminations

2.6.1.1           	The input terminals shall be clearly marked as R, Y, B & N for three phase and L and N for single phase as applicable.

2.6.1.2       	AC input termination shall be suitably protected against   the accidental touch/contact with the working staff for their protection & shall also have clear & prominent "DANGER" marking. AC terminations shall be through standard finger safe lock-in type connectors conforming to BIS or any other international standard, with the concurrence of CACT.

2.6.1.3       	Screening shall be provided   between AC & DC components   to prevent accident.

2.6.1.4         	The AC input connection to the rectifier module shall be by a composite type hot plug-in connectors and socket arrangement.

2.6.1.5         	All the connections between Distribution and FR/FC, shall  be  through proper rated cables only.

2.6.1.6         	Fuses   and   Circuit-breakers   for   each   FR/FC, FR/BC  shall   be  easily accessible and properly rated.

2.6.1.7          Proper terminations for AC at the input of the circuit-breakers and its output to the FR/FC.

2.6.2              	DC Terminations

2.6.2.1           	The male connectors shall   be mounted in the FR/FC, FR/BC module and female connectors be terminated to the cable.

2.6.2.2	The DC output to Battery and Load shall be through cable/bus-bars up to the rack capacity of 450A ultimate capacity and bus-bar only for higher capacities or as per users requirement. However for inter-rack connections, cables of proper rating are permitted.

2.6.2.3         	The provision for interconnection between exchange and  FR/FC, FR/BC  or battery (along with switching arrangement) and terminations for Exchange,  Battery  & FR/FCs, FR/BCs shall be made. The isolation of any of the battery from the load shall create an alarm.

2.6.2.4            All DC + ve and – ve leads shall be clearly marked.

2.6.3              	All the AC, DC Control & alarm cabling shall be supplied with  the rack.

2.7                 	Bus Bars

Tinned Bus-bars or tinned High conductivity electrolytic  copper  strips  with purity of 99.90% (min) as per BIS 613 latest  issue, be  able  to  withstand maximum Load current. The Bus-bar shall be capable to carry current density of 2 Amps/mm square but shall not be less than 25mmX5mm in any case. Nuts & bolts shall be of stainless steel with tinned copper washers only. The size of bus-bars chosen for battery and load path shall be capable to take care of the current of maximum power plant capacity for which it is designed. The Bus-bar/cable size shall also ensure that the voltage drop between the output of the farthest FR/FC module riser and also between battery and exchange riser, as per the layout drawing shall be less than 500mV.  The tinning shall be in compliance of IS 1359: 1992 and its thickness shall be 10 m (minimum).

2.7.1            	Bus-bar Riser height, wherever applicable, shall be 250 mm for both exchange and battery. Bus-bar Riser should be used for higher capacity of exchange load and battery more than 450 Amp. There shall be no bus-bar in outdoor units.

2.8                	Cabling and Wiring

All  insulated   conductors     except     those  within  the  confines  of  a printed   circuit   board  assembly shall be of the rating  enough  to withstand  the maximum current and voltage during fault and  overload.  All the wires and cables used shall be fire retardant as per IS 1554 with amendment 1 (June 94). All the cables & wires used shall also be Rodent & reptiles repellent.

2.8.1              	All wiring shall be neatly   secured in    position   and adequately supported.  Where wires pass through any part of metal panel or cover     the hole through which they pass shall be suitably bushed.

2.9            	Earthing

Proper Earth terminal (two in each rack), in effective electrical contact with framework, shall be provided.  All metal parts of the components, which do not carry current, shall be bonded thereto. Nominal cross-sectional area of earth continuity conductor, not contained within the cable, shall be half (minimum) of each current carrying conductor to be protected but in no case it shall be less than 3 mm diameter. Continuity conductor used for the purpose shall only be of copper.  Suitable terminals shall be provided for terminating earth conductor.

2.10                Mounting of component & layout

2.10.1            	Component mounting and fixing methods shall be secured.

2.10.2            	Suitable   mechanical   structure/ arrangement for holding  modules in  position  shall be  provided so that the module is held  firmly  by sliding through it.

2.11            	Documentation

Technical literature in English and Hindi with complete layout, detailed block schematic and circuit diagrams of its assemblies with test voltages at different test points of the units shall be provided. A soft copy as well as a hard copy of the above shall also be provided. All aspects of installation, operation, maintenance, trouble shooting and repair shall be covered in this manual. The manual shall also include the following:

a) 		Installation, Operation and Maintenance manual part shall include:

i)  Safety measures to be observed in handling of the equipment.

ii)  Precautions at the time of installation, operation and maintenance.

iii)  Required Test Jigs and fixtures.

iv) Procedures for routine maintenance, preventive maintenance, trouble shooting and replacement.

v)  Illustration of internal and external mechanical parts.

vi)  Complete   layout, detailed block schematic and circuit diagrams of its    assemblies with test voltages at different test points.

vii) Circuit description and working of FR/FC module at various stages staring from AC mains input to the DC output with Block Schematic.

- Circuit description and working of DSCA.

ix) Instructions for the termination of Temperature Compensation Probes at DSCA as well as battery.

x) A Table giving details of size/dimension of maintenance of cables and Bus-bar used in the design.

xi)  Earthing Guide lines for the Power Plant as per BIS Specification.

xii) Co-ordination distance (length & gauge of the cable to be used)/ de-coupling inductance between stage –I & Stage – II surge protection.

- Repair manual  :

  - List of replaceable parts used with the source of procurement.

  - Detailed ordering information for all replaceable parts for ordering of spares as and when required.

  - Procedure with flowchart for trouble shooting and sub-assembly replacement.

  - Test Instruments, Test fixtures, accessories and tools required  for maintenance and repair.

  - Systematic trouble shooting charts (fault tree) for probable faults and their remedial action.

  - Address and telephone numbers of Maintenance centre.

2.11.1          	Hard copy of the documentation shall be prepared using good quality paper with clear and crisp printing. All the drawings in clear printing shall be attached to the hand-book binding. The binding of the manual shall be long lasting and presentable. One set of flow chart drawings necessary for  trouble-shooting  shall  be provided  with lamination, with each manual.

2.12              	Quality Requirements

2.12.1          	Components: The component parts of the equipment shall be of professional grade of reputed manufacturer to ensure prompt and continuous service and delivery of spare parts. Use of potentiometer is precluded. Switching components used on the input side shall be rated at 600V (minimum)

2.12.1.1        	Power transformers and Chokes: Power transformers & chokes shall use class B or higher grade of insulation. The transformers and chokes shall be wound with copper wire and provided with adequate insulation.

2.12.1.2     	Fuses or circuit breakers shall be provided wherever appropriate for the protection against failure of control/sensing circuit. Fuses shall conform to B.I.S specification.

2.12.1.3         	Meters: There shall be provision to monitor AC voltage of the system and DC current as well as  voltage with the help of Digital meters to  read the voltage  and current of the System, any of the Battery or any  of  the individual FR/FC (at individual FR/FC module also  permitted).  Digital meter’s display/resolution should be such that it is clearly and unambiguously readable from a distance of 1 metre. Normally the meters mounted at DSCA shall indicate the System voltage and current.

a. Current:  +/- 1.5% of the range or better, shall be able to read up to full digit for meter range 50A & above and 1 place decimal for lower meter range.

b. Voltage:  +/- 1.5% of the range or better with a  resolution  of  one decimal point in case of DC voltmeter and full digit in  case  of AC voltmeters.

2.12.1.4        	Component Approval: The components used in SMPS Power Plant, shall be certified by recognised National/International Institutions and approved by CACT wing of BSNL. Components shall neither be combustible nor support combustion.

2.12.2             Quality and Workmanship:

a) The equipment shall manufacture in accordance with international quality management systems ISO-9001-2000, for which the manufacturer shall be duly accredited. A quality plan describing the quality assurance system followed by the manufacturer would be required to be submitted.

b) The equipment shall be manufactured as per the latest BSNL QA Guidelines indicated in Quality Manuals QM-118 (Quality reliability in product design), Manuals QM-202 ( Pictorial  guidelines  for  Visual   assessment of quality of printed board assemblies  (PBA) and discrete terminal assemblies), QM-204 (Guidelines for workmanship standards for repair & modification of printed wiring  board assemblies), QM-205 (Guidelines for standard of workmanship for printed boards), QM-206 (Guidelines for standard of workmanship for printed boards assemblies), QM-207 (Guidelines for soft solder and fluxes for Telecom Equipments)  and QM 210 (Guidelines for standard of workmanship for surface Mounting Devices).

All wiring   shall be neatly secured in position and adequately supported.  Metal panel or cover holes through which the wires or cables pass shall be suitably bushed.

c) All materials   and workmanship shall be of professional quality to ensure the MTBF requirements.

2.12.3           	Quality   Assurance Tests:  Each of the units supplied against the specific order after type approval shall be inspected and tested to   ensure that the requirements of this document have been met.  These   tests shall be carried out by QA wing of BSNL.

2.12.4           	Finish and painting: The finish of the structure and panels shall conform to the latest issue of IS 101 and IS 168. The structure and panels shall only be powdered coated. The thickness of powder coating shall be between 50 to 70 micrometers. The Colour used shall conform to IS 5 latest issue. Colour scheme shall be as follows:

a. Rack & Door: Satin Blue, No.  177

b. Modules and inside: Shall harmoniously match with rack colour

2.12.5             Marking and Labelling:

2.12.5.1        	It   shall   be   possible to locate each component on the PCB with the help of layout and circuit drawing. All terminals shall be properly sign-written and all components properly labelled so that it shall be easy to identify them with reference to the supplier's Instruction and Maintenance Manuals. Designation of keys, switches and other components mounted on the front/inside panel and their operating positions shall be clearly engraved or sign- written. The wiring shall be clearly and permanently identified with the designation or colour code which corresponds to the equipment circuit diagram. Where non-standard colours are used cable functions shall be clearly and permanently labelled at both ends.

2.12.5.2         	Fuse    holder   identification   shall include details of fuse rating and type. In case of fuses on PCBs the rating shall be either on the fuse or PCB.

2.12.5.3         	A   cabling    diagram,   screen   printed    or  any  other  better  arrangement  ensuring  better life expectancy shall be placed  in  the  inside  of  the  front door or any other convenient  place  for  ready reference of the maintenance staff.

2.13          	Name plate

A  name plate anodised, screen printed or any  other  better  arrangement  ensuring better life expectancy shall be  suitably  fixed on each rack & module and contain following information :

1. Specification Number:

2. Type of the Unit:

3. Manufacturer's name and identification:

4. Model No.       :

5. Unit Serial No. :

6. TAC No.

7. Input voltage and phase:

8. Output Voltage and Current:

9. Year of manufacture:

2.13.1          	On the front top of the Rack an anodised, screen printed  or any  other  better  arrangement  ensuring better life expectancy Designation plate in BOLD letters showing “ LARGE / SMALL CAPACITY SMPS POWER PLANT  SYSTEM, COMPATIBLE WITH VRLA / (VRLA AND CONVENTIONAL LEAD ACID)  BATTERIES ” shall be provided.

2.14               	Module Replacement Time & MTBF

2.14.1         	Module Replacement Time:  The mean time to replace a faulty rectifier module shall be less than 20 minutes.

2.14.2           	MTBF (Mean Time between Failures): MTBF of the system shall not be less than 100,000 hours. The MTBF for fans shall be better than 70,000 hours at 40 degree C. The concurrence of CACT of QA wing of BSNL in this regard is mandatory. The MTBF shall be verified as per QM-115.  MTBF, predicted and observed values shall be furnished along with calculations by the manufacturer. Based on these figures three years maintenance spares shall be specified by the equipment supplier. The equipment availability shall exceed 99.9%.

2.15                    Field Observations

For new products field observation may be carried out by purchaser

2.16	Packing

Packing shall be done in accordance with latest guidelines for the SMPS Power Plants issued by QA wing of BSNL.

2.17		Environmental requirements

Each system shall be capable of operating in conditions conforming to QM-333 category B2 of QA Wing of BSNL. It shall also comply with vibration requirements of clause 12.0 of QM-333. The system shall also be capable of working in saline atmosphere of coastal areas and up to an altitude of 3000 Metres in compliance of QM-333.  The environmental tests shall be performed by configuring the power plant as follows:

(i)	DSCA for ultimate capacity

(ii)	One FR/FC, FR/BC (Conventional Battery Power Plant) module

2.17.1		Burn-in tests

The fully equipped rack shall be capable of withstanding a burn-in test for 72 hours at an ambient temperature of 50C when the equipment is working at full rated load. This test may be performed in a temperature controlled room with free air flow.  The ambient temperature shall be measured at a distance of 1 foot from the equipment under test. The necessary set-up for the purpose shall be provided by the manufacturer.

The temperature rise of the heat dissipating components  above  the ambient, measured directly or at heat sink in the first eight hours of the test, shall not be more than :

a) 	Transformers and Chokes: 70 deg C for Grade B insulation.

For higher grade of insulation, higher temperature rise may be permissible, subject to the following conditions:

(i)	It is at least 20 deg C below the permissible limit for the grade of insulation used.

(ii)	The temperature rise shall be at least 30 deg C below Curie temperature of the magnetic material.

(iii)	This temperature shall neither affect other components nor shall lead to fire hazard.

b) 	Semiconductor devices: 60 deg C or as per component spec.

2.17.2	Insulation Resistance and Voltage Proof Tests:

2.17.2.1	The insulation resistance test

The insulation resistance of a fully wired FR/FC, when tested with a 500V DC megger, shall be as given below:

a)	AC Input & Earth - Greater than 2 meg Ohm

b)	DC Output & Earth - Greater than 1 meg Ohm

c) 	AC Input & DC out put - Greater than 5 meg Ohm

1.	2.17.2.2      	Voltage   Proof    Test

With EMI/RFI capacitors and MOVs/Tranzorbs removed from the circuit a test voltage of 1500V/50Hz is applied for one minute.

-  Between earth and interconnected output terminals.

-  Between interconnected input and output terminals.

Alternatively, without removing EMI/RFI capacitors, the lightning protection circuitry and Tranzorbs etc., but with EMI/RFI discharge resistors removed:

a)	A 2150V DC can be applied for one minute between interconnected input & output terminals.

b) 	650V DC can be applied for one minute between interconnected output terminals & earth.

This DC voltage test is in accordance with UL 950 & IEC 950 Standards. No breakdown or abnormal temperature rise shall occur.

2.17.3        		Noise   and   Vibration

The fully equipped rack at full load shall not contribute more than 15 dB (weighted) to the ambient noise level taken as 45dBA. It shall be measured at a distance of 1 metre from the   unit & 1.25m above the floor level in the Acoustic Range. The correction factor for Total Noise when the ambient noise level is more than 45dBA, shall be as given below:

| Ambient Noise | Correction Factor | Ambient Noise | Correction Factor | Ambient Noise | Correction Factor |
| --- | --- | --- | --- | --- | --- |
| 45dBA | 0dB | 51dBA | 1.41dB | 57dB | 3.69dB |
| 46dBA | 0.18dB | 52dBA | 1.73dB | 58dB | 4.17dB |
| 47dBA | 0.39dB | 53dBA | 2.07dB | 59dB | 4.68dB |
| 48dBA | 0.61dB | 54dBA | 2.43dB | 60dB | 5.21dB |
| 49dBA | 0.86dB | 55dBA | 2.82dB |  |  |
| 50dBA | 1.12dB | 56dBA | 3.25dB |  |  |

Note: The correction Factor shall be added to the limit of 60 dBA to arrive at the limit when the ambient is greater than 45 dBA.

- PART 3

- Guidelines for the Purchaser/User

- No.: BSNL/Specification/SMP - 001/01/March.2014

3.0		Guidelines for the Purchaser/User

3.1	The purchaser must ensure the availability of separate coordinated Stage-I & II protection devices, as per GR No. TEC/GR/FLA/LSP - 01.June.2010 at telecom site, for protection of the Power Plant, against lightening and high voltage surges.

3.2            	The purchaser shall specify the requirement and dimensions for Single Rack and/or Auxiliary Rack, depending on the needs of expansion and ultimate capacity. The type of rack – floor mounted or wall mounted – shall also be specified.

3.3	The purchase may specify the requirement of field-trial. Feedback, if any, may be furnished to TEC for improvement in the GR.

3.4	The purchaser shall specify the requirements for optional management features like Battery Health Monitoring, Energy Saving Management, proper functioning during voltage and phase outages, DG Efficiency & Fuel Saving Management, Battery Efficiency & Battery Management, Rectifier Control – Efficiency Management, etc.

ANNEXURE - 1

Protocol or Sequence of Exchange of Information between Power plant & Remote Site monitoring equipment

RS 485 (4 wire) interface at speed 19.2Kbps (minimum) shall be used for both monitoring & control between power plants  and Remote site (First level)  of monitoring & control. The protocol shall be as given below ;

-  First four bytes as starting or hand shake bites (includes identifications etc.)

-  5th  Byte for equipment Identification (Power plant battery, Inverter etc.)

-  6th Byte  for  Class of parameter  (Alarms urgent, alarms non-urgent, Monitoring etc.)

-  7th ,8th and 9th Bytes for the  parameter observation/medications :

Equipment side will  send parameter code ( same that on Master side) along with  desired information.

-  10th and 11th   for checksum for  parity on both sides in communication.

The exchange of information between the  Remote site controller and the power  equipment  shall on 4 wire RS 485 bus.   All the eleven bytes  shall be sent as a packet for exchange of information.

In this concept Remote site equipment shall work as a Master and power equipment as slave in the Master slave concept.  In this concept:

-  	The master will send all the above 11 bytes containing the information for each byte as given above..

-  	Power  Equipment  after verify the correctness of the data will send back the  desired information in the same pattern as given above  with  bytes 7 to 9 shall contain the desired information and 10th 11th the checksum number.

-  	In case of mismatch, power equipment or remote controller will send a fixed anomaly signal.

-  	On receipt of mismatch the previous data will again be offered by the concerned end.

-  	In case of acknowledgement (desired information or next information) the concerned end will put-up the next information.

Each byte information in HEX shall be as detailed below:

5th Byte:   Equipment Designation

| Equipment Designation | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Power Plant s(AC-DC Converters) ( sixteen Max.) | 00 to 0F | 00 to 0F |
| Battery Bank ( Maximum sixteen) | 10 to 1F | 10 to 1F |

6th Byte: Classification of Information

| Class of Parameter | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Alarms Urgent | 01 | 01 |
| Alarms Non-urgent | 02 | 02 |
| Monitoring of Parameters | 03 | 03 |
| Parameter Control | 04 | 04 |
| System Details | 05 | 05 |
| Any other information | 06 to FF | 06 to FF |

7th to 9th Byte : Parameter name :

- Power Plant ( 5th byte  :  00 to 0F)

i)     Alarms Urgent (6th byte   :  01)

| Parameter Name |  | Hex Code |  |
| --- | --- | --- | --- |
|  |  | From Master | From Slave Equipment |
| Mains "ON"/Battery Discharging - Any reason for failure of Power plant to deliver the output (including AC input contactor failure) | 01, 00, 00 |  | 01, 01, 00 : OK 01, 02, 00 : FAULT |
| System Over Load | 02, 00, 00 |  | 02, 01, 00 : OK 02, 02, 00 : FAULT |
| Load Voltage High | 03, 00, 00 |  | 03, 01, 00 : OK 03, 02, 00 : FAULT |
| Load Voltage Low | Same sequence |  | Same sequence |
| Fan Fail – Rack | Same sequence |  | Same sequence |
| Battery 1 : Temp. Compensation fail | Same sequence |  | Same sequence |
| Battery 2 : Temp. Compensation fail | Same sequence |  | Same sequence |
| ------------------------------------------------- | Same sequence |  | Same sequence |
| Battery 5 : Temp. Compensation fail | Same sequence |  | Same sequence |
| Battery 1 Fail OR No Battery | Same sequence |  | Same sequence |
| Battery 2 Fail OR No Battery | Same sequence |  | Same sequence |
| ………………………………………. | Same sequence |  | Same sequence |
| Battery 5 Fail OR No Battery | Same sequence |  | Same sequence |

ii) Alarms Non-Urgent (Sixth Byte:   02)

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Mains High | 01, 00, 00 | 01, 01, 00 : OK 01, 02, 00 : FAULT |
| Mains Low | 02, 00, 00 | 02, 01, 00 : OK 02, 02, 00 : FAULT |
| FR/FC 1 –Over Voltage | 03, 00, 00 | 03, 01, 00 : OK 03, 02, 00 : FAULT |
| FR/FC 2 –Over Voltage | Same sequence | Same sequence |
| ……………… | Same sequence | Same sequence |
| FR/FC 30 –Over Voltage | Same sequence | Same sequence |
| FR/FC 1 –Under Voltage/Output Fail | Same sequence | Same sequence |
| FR/FC 2 –Under Voltage/Output Fail | Same sequence | Same sequence |
| …………….. | Same sequence | Same sequence |
| FR/FC 30 –Under Voltage/Output Fail | Same sequence | Same sequence |
| FR/FC 1 –Over Load | Same sequence | Same sequence |
| FR/FC 2 –Over Load | Same sequence | Same sequence |
| ………………….. | Same sequence | Same sequence |
| FR/FC 30 –Over Load | Same sequence | Same sequence |
| Fan Fail - FR/FC 1 | Same sequence | Same sequence |
| Fan Fail - FR/FC 2 | Same sequence | Same sequence |
| ………. | Same sequence | Same sequence |
| Fan Fail - FR/FC 30 | Same sequence | Same sequence |
| FR/FC 1 – Fail | Same sequence | Same sequence |
| FR/FC 2 – Fail | Same sequence | Same sequence |
| ………. | Same sequence | Same sequence |
| FR/FC 30- Fail | Same sequence | Same sequence |
| Any other Alarm condition | Same sequence | Same sequence |

iii) Monitoring Parameters (6th byte   :   03)

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Power plant on Mains/Standby | 01, 00, 00 | 01, 01, 00 : MAINS 01, 02, 00 : STAND BY |
| Load on power plant/Battery | 02, 00, 00 | 02, 01, 00 : Power Plant 02, 02, 00 : Battery |
| AC Mains Voltage | 03, 00, 00 | 03, VALUE(H), VALUE(L) |
| System Output Voltage | 04, 00, 00 | 04, VALUE(H), VALUE(L) |
| System Load | 05, 00, 00 | 05, VALUE(H), VALUE(L) |
| FR/FC 1 – Load | Same sequence | Same sequence |
| FR/FC 2 – Load | Same sequence | Same sequence |
| ………………………. | Same sequence | Same sequence |
| FR/FC 30 – Load | Same sequence | Same sequence |
| Battery 1 Path Current | Same sequence | Same sequence |
| Battery 2 path current | Same sequence | Same sequence |
| ------------------------------ | Same sequence | Same sequence |
| Battery 5 path Current | Same sequence | Same sequence |
| Load sharing performance (%) | Same sequence | Same sequence |
| Any other Monitoring requirements | Same sequence | Same sequence |

- Parameter Control (Sixth Byte  :  04)

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Mains High | 01, VALUE(H), VALUE(L) | 01, VALUE(H), VALUE(L) |
| Mains Low | 02, VALUE(H), VALUE(L) | 02, VALUE(H), VALUE(L) |
| System Over Load (Value) | 03, VALUE(H), VALUE(L) | 03, VALUE(H), VALUE(L) |
| System Float Voltage | 04, VALUE(H), VALUE(L) | 04, VALUE(H), VALUE(L) |
| System Charge Voltage | 05, VALUE(H), VALUE(L) | 05, VALUE(H), VALUE(L) |
| Load Voltage High | Same sequence | Same sequence |
| Load Voltage Low | Same sequence | Same sequence |
| Battery 1 Path Current Limit | Same sequence | Same sequence |
| Battery 2 path current Limit | Same sequence | Same sequence |
| ---------------------------------------- | Same sequence | Same sequence |
| Battery 5 path Current Limit | Same sequence | Same sequence |
| FR/FC 1 –Float Voltage | Same sequence | Same sequence |
| FR/FC 2 –Float Voltage | Same sequence | Same sequence |
| ---------------------------------------- | Same sequence | Same sequence |
| FR/FC 30 –Float Voltage | Same sequence | Same sequence |
| FR/FC 1 –Charge Voltage | Same sequence | Same sequence |
| FR/FC 2 – Charge Voltage | Same sequence | Same sequence |
| ----------------------------------------- | Same sequence | Same sequence |
| FR/FC 30 –Charge Voltage | Same sequence | Same sequence |
| FR/FC 1 –Over Voltage | Same sequence | Same sequence |
| FR/FC 2 –Over Voltage | Same sequence | Same sequence |
| -------------------------------------------- | Same sequence | Same sequence |
| FR/FC 30 –Over Voltage | Same sequence | Same sequence |
| FR/FC 1 –Under Voltage | Same sequence | Same sequence |
| FR/FC 2 –Under Voltage | Same sequence | Same sequence |
| ------------------------------------------- | Same sequence | Same sequence |
| FR/FC 30 –Under Voltage | Same sequence | Same sequence |
| FR/FC 1 –Over Load | Same sequence | Same sequence |
| FR/FC 2 –Over Load | Same sequence | Same sequence |
| ------------------------------------------ | Same sequence | Same sequence |
| FR/FC 30 –Over Load | Same sequence | Same sequence |
| Any other parameter to control | Same sequence | Same sequence |

Note : 1. If the remote controller  wants to check the current setting, it shall  send 8th and 9th bytes as 00 00 along with the data of 7th byte as given above, the  associated equipment shall return the current value.

2. If the associated equipment returns the same value as sent by controller it shall be taken as accepted otherwise not accepted and shall be resent after  doing the needful.

v)  System details (sixth byte  :   05)  :

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| System Make | May be generated in the remote controller by manual inputting |  |
| Date of commissioning | May be generated in the remote controller by manual inputting |  |
| System Ultimate capacity | 03,00,00 | 03, VALUE(H), VALUE(L) |
| System Equipped capacity | 04,00,00 | 04, VALUE(H), VALUE(L) |
| Number of FR/FCs | Same sequence | Same sequence |
| Rating of FR/FCs | Same sequence | Same sequence |
| Number of FR/FC Working | Same sequence | Same sequence |
| Number of FR/FC Faulty | Same sequence | Same sequence |
| Number of batteries connected with the power plant | Same sequence | Same sequence |
| Battery 1 : Make | May be generated in the remote controller by manual inputting |  |
| Date of Commissioning | May be generated in the remote controller by manual inputting |  |
| AH Capacity | May be generated in the remote controller by manual inputting |  |
| Battery 2 : Make | Same sequence | Same sequence |
| Date of Commissioning | Same sequence | Same sequence |
| AH Capacity | Same sequence | Same sequence |
| ---------------------------------------- | Same sequence | Same sequence |
| Battery 5 : Make | Same sequence | Same sequence |
| Date of commissioning | Same sequence | Same sequence |
| AH Capacity | Same sequence | Same sequence |

Note :  In case the above information can not be provided by the associated  equipment,  same may  be generated in the  First stage system  by manually  in-putting the data.

b) Battery Parameters (5th Byte:  10 to 1F):

- Alarms  Urgent (sixth byte as 01)

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Battery 1 : Voltage OK/High/LOW | 01, 00, 00 | 01, 01, 00 : OK 01, 02, 00 : High 01, 03, 00 : Low |
| Temperature OK/High/Low | 02, 00, 00 | 02, 01, 00 : OK 02, 02, 00 : High 02, 03, 00 : Low |
| Trickle Current OK/High (As per set value) | 03, 00, 00 | 03, 01, 00 : OK 03, 02, 00 : High |
| Battery Current OK/High ( As per limit set) | 04, 00, 00 | 04, 01,00 : OK 04, 02, 00 : High |
| Cell 1Failing (Voltage High/ low, conductance out of range low high/ Low, Temp High/low as compared to other cells) | Same sequence | Same sequence |
| Cell 2 Failing | Same sequence | Same sequence |
| ……………………….. | Same sequence | Same sequence |
| Cell 24 Failing | Same sequence | Same sequence |
| Battery 2 : Voltage OK/High/LOW | Same sequence | Same sequence |
| Temperature OK/High/Low | Same sequence | Same sequence |
| Trickle Current OK/High (As per set value) | Same sequence | Same sequence |
| Battery Current OK/High ( As per limit set) | Same sequence | Same sequence |
| Cell 1 Failing | Same sequence | Same sequence |
| Cell 2 Failing | Same sequence | Same sequence |
| ……………………….. | Same sequence | Same sequence |
| Cell 24 Failing | Same sequence | Same sequence |
| ---------------------------------------------------------------- | Same sequence | Same sequence |
| Battery 5 : Voltage OK/High/LOW | Same sequence | Same sequence |
| Temperature OK/High/Low | Same sequence | Same sequence |
| Trickle Current OK/High (As per set value) | Same sequence | Same sequence |
| Battery Current OK/High ( As per limit set) | Same sequence | Same sequence |
| Cell 1 Failing | Same sequence | Same sequence |
| Cell 2 Failing | Same sequence | Same sequence |
| ……………………….. | Same sequence | Same sequence |
| Cell 24 Failing | Same sequence | Same sequence |
| Any other Alarm Conditions | Same sequence | Same sequence |

Note: 1. 	All the cells  which are showing  failing tendency during  routine observation or during discharge test  shall be reported as an Urgent alarm.

2.	There shall be provision  to set the battery to discharge  for a certain duration, during  which the  voltage, current  and conductance out of range of each cell shall be recorded. Deviation from the bench mark  value shall be high lighted as an alarm.

3. 	Trickle current during battery float operation shall be observed and high trickle current higher than the  set threshold shall create  an Urgent alarm.

- Alarms Non-Urgent (Sixth Byte as 02)

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Battery on discharge | 01, 00, 00 | 01, 01, 00 : NO 01, 02, 00 : YES |
| Any other Alarm condition | Same sequence | Same sequence |

- Monitoring Parameters (Sixth Byte as 03)

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Battery 1 : State of Charge battery ( %) | 01, 00, 00 | 01, Value (H), Value (L) |
| Voltage battery | 02, 00, 00 | 02, Value (H), Value (L) |
| Voltage - cell1 | 03, 00, 00 | 01, Value (H), Value (L) |
| Voltage - cell 2 | 04, 00, 00 | 01, Value (H), Value (L) |
| ------------------- | Same sequence | Same sequence |
| Voltage cell 24 | Same sequence | Same sequence |
| Temperature Battery | Same sequence | Same sequence |
| Temperature cell1 | Same sequence | Same sequence |
| Temperature cell 2 | Same sequence | Same sequence |
| ----------------------- | Same sequence | Same sequence |
| Temperature cell 24 | Same sequence | Same sequence |
| conductance out of range out of range Battery | Same sequence | Same sequence |
| Conductance out of range cell1 | Same sequence | Same sequence |
| Conductance out of range cell 2 | Same sequence | Same sequence |
| ----------------------- | Same sequence | Same sequence |
| Conductance out of range cell 24 | Same sequence | Same sequence |
| Battery 2 : State of Charge Battery ( %) | Same sequence | Same sequence |
| Voltage Battery | Same sequence | Same sequence |
| Voltage - cell1 | Same sequence | Same sequence |
| Voltage - cell 2 | Same sequence | Same sequence |
| ------------------- | Same sequence | Same sequence |
| Voltage cell 24 | Same sequence | Same sequence |
| Temperature Battery | Same sequence | Same sequence |
| Temperature cell1 | Same sequence | Same sequence |
| Temperature cell 2 | Same sequence | Same sequence |
| ----------------------- | Same sequence | Same sequence |
| Temperature cell 24 | Same sequence | Same sequence |
| Conductance out of range Battery | Same sequence | Same sequence |
| Conductance out of range cell1 | Same sequence | Same sequence |
| Conductance out of range cell 2 | Same sequence | Same sequence |
| ----------------------- | Same sequence | Same sequence |
| Conductance out of range cell 24 | Same sequence | Same sequence |
| -------------------------------------------------------- | Same sequence | Same sequence |
| Battery 5 : State of Charge battery ( %) | Same sequence | Same sequence |
| Voltage battery | Same sequence | Same sequence |
| Voltage - cell1 | Same sequence | Same sequence |
| Voltage - cell 2 | Same sequence | Same sequence |
| ------------------- | Same sequence | Same sequence |
| Voltage cell 24 | Same sequence | Same sequence |
| Temperature Battery | Same sequence | Same sequence |
| Temperature cell1 | Same sequence | Same sequence |
| Temperature cell 2 | Same sequence | Same sequence |
| ----------------------- | Same sequence | Same sequence |
| Temperature cell 24 | Same sequence | Same sequence |
| Conductance out of range Battery | Same sequence | Same sequence |
| Conductance out of range cell1 | Same sequence | Same sequence |
| Conductance out of range cell 2 | Same sequence | Same sequence |
| ----------------------- | Same sequence | Same sequence |
| Conductance out of range cell 24 | Same sequence | Same sequence |
| Any other parameter to be monitored | Same sequence | Same sequence |

- Parameter Control (Sixth Byte as 04)

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Battery 1 : Trickle current Limit | 01, Value (H), Value (L) | 01, Value (H), Value (L) |
| Voltage limit for alarm | 02, Value (H), Value (L) | 02, Value (H), Value (L) |
| Charge Current limit for alarm | 03, Value (H), Value (L) | 03, Value (H), Value (L) |
| Temperature limit for alarm | Same sequence | Same sequence |
| Conductance out of range Limit for Alarm | Same sequence | Same sequence |
| Cell 1 : Voltage limit for alarm | Same sequence | Same sequence |
| Cell 2 : Voltage limit for alarm | Same sequence | Same sequence |
| ----------------------------------------- | Same sequence | Same sequence |
| Cell 24 : Voltage limit for alarm | Same sequence | Same sequence |
| Cell 1 : Temperature limit for Alarm | Same sequence | Same sequence |
| Cell 2 : Temperature limit for alarm | Same sequence | Same sequence |
| ------------------------------------------- | Same sequence | Same sequence |
| Cell 24 : Temperature limit for alarm | Same sequence | Same sequence |
| Cell 1 : conductance out of range limit for alarm | Same sequence | Same sequence |
| Cell 2 : conductance out of range limit for alarm | Same sequence | Same sequence |
| ------------------------------------------------ | Same sequence | Same sequence |
| Cell 24 : conductance out of range limit for alarm | Same sequence | Same sequence |
| Battery 2 : Trickle current Limit | Same sequence | Same sequence |
| Voltage limit for alarm | Same sequence | Same sequence |
| Charge Current limit for alarm | Same sequence | Same sequence |
| Temperature limit for alarm | Same sequence | Same sequence |
| conductance out of range Limit for Alarm | Same sequence | Same sequence |
| Cell 1 : Voltage limit for alarm | Same sequence | Same sequence |
| Cell 2 : Voltage limit for alarm | Same sequence | Same sequence |
| ---------------------------------------- | Same sequence | Same sequence |
| Cell 24 : Voltage limit for alarm | Same sequence | Same sequence |
| Cell 1 : Temperature limit for Alarm | Same sequence | Same sequence |
| Cell 2 : Temperature limit for alarm | Same sequence | Same sequence |
| ------------------------------------------- | Same sequence | Same sequence |
| Cell 24 : Temperature limit for alarm | Same sequence | Same sequence |
| Cell 1 : conductance out of range limit for alarm | Same sequence | Same sequence |
| Cell 2 : conductance out of range limit for alarm | Same sequence | Same sequence |
| ----------------------------------------------- | Same sequence | Same sequence |
| Cell 24 : conductance out of range limit for alarm | Same sequence | Same sequence |
| -------------------------------------------------- | Same sequence | Same sequence |
| Battery 5 : Trickle current Limit | Same sequence | Same sequence |
| Voltage limit for alarm | Same sequence | Same sequence |
| Charge Current limit for alarm | Same sequence | Same sequence |
| Temperature limit for alarm | Same sequence | Same sequence |
| conductance out of range Limit for Alarm | Same sequence | Same sequence |
| Cell 1 : Voltage limit for alarm | Same sequence | Same sequence |
| Cell 2 : Voltage limit for alarm | Same sequence | Same sequence |
| ------------------------------------------- | Same sequence | Same sequence |
| Cell 24 : Voltage limit for alarm | Same sequence | Same sequence |
| Cell 1 : Temperature limit for Alarm | Same sequence | Same sequence |
| Cell 2 : Temperature limit for alarm | Same sequence | Same sequence |
| ------------------------------------------- | Same sequence | Same sequence |
| Cell 24 : Temperature limit for alarm | Same sequence | Same sequence |
| Cell 1 : conductance out of range limit for alarm | Same sequence | Same sequence |
| Cell 2 : conductance out of range limit for alarm | Same sequence | Same sequence |
| ------------------------------------------------ | Same sequence | Same sequence |
| Cell 24 : conductance out of range limit for alarm | Same sequence | Same sequence |
| Any other parameter to set | Same sequence | Same sequence |

Note: 1.    If  the remote controller  wants to check the current setting, it shall  send 8th and 9th bytes as 00 00 along with the data of 7th byte as given above, the  associated equipment shall return the current value.

2.   If the associated equipment returns the same value as sent by controller it shall be taken as accepted otherwise not accepted and shall be resent after  doing the needful.

- System details (Sixth Byte as 05) :

| Parameter Name | Hex Code |  |
| --- | --- | --- |
|  | From Master | From Slave Equipment |
| Number of Batteries in the bank | 01, 00, 00 | 01, Value (H), Value (L) |
| Battery 1 : Make | May be generated in the remote controller by manual inputting |  |
| Date of Commission of battery | May be generated in the remote controller by manual inputting |  |
| AH Capacity | 04, 00, 00 | 04, Value (H), Value (L) |
| Battery 2 : Make | Same sequence as for Bat. 1 | Same sequence as for Bat. 1 |
| Date of Commission of battery | Same sequence as for Bat. 1 | Same sequence as for Bat. 1 |
| AH Capacity | Same sequence as for Bat. 1 | Same sequence as for Bat. 1 |
| ---------------------------------------- | Same sequence as for Bat. 1 | Same sequence as for Bat. 1 |
| Battery 5 : Make | Same sequence as for Bat. 1 | Same sequence as for Bat. 1 |
| Date of Commission of battery | Same sequence as for Bat. 1 | Same sequence as for Bat. 1 |
| AH Capacity | Same sequence as for Bat. 1 | Same sequence as for Bat. 1 |
| Any other information | Same sequence as for Bat. 1 | Same sequence as for Bat. 1 |

Note:	In case the above information can not be provided by the power plant or battery controller the same will be

generated in the  First stage system.

ANNEXURE - 2

ORDERING INFORMATION

The following items need to be specified while ordering by Tendering Authority depending on the requirements.

- Application:

AC Input:   Single phase

Three Phase

Rack Height:    1500mm

2200mm

- Category and Ultimate capacity  of power plant  as per clause 2.2.3

- Rating of the basic module:  25A/50A/100A/200A as per Category.

- Number of basic modules required at present including redundant units.

- Power Plant Compatible with VRLA batteries only or with both VRLA and   conventional batteries.

- Remote Monitoring requirements: Required/Not Required

- Battery Health Check requirements: Required/not required

- Capacity of the battery proposed in Ampere Hours.

- Number of batteries proposed at present and ultimate.

Important Notes:

- Load shall include equipment load, battery load at C/10 rate of charge and other load (inverter etc.) if any.

- While choosing the power plant the user shall ensure that the redundancy requirement has been taken care of.

3. 	It may be ensured that minimum two Batteries are chosen to meet the load requirement.

Abbreviations

A or Amps	Amperes

AC	Alternate Current

AH	Ampere Hour

BIS	Bureau of Indian Standards

BSNL	Bharat Sanchar Nigam Limited

CACT	Component Approval Centre of Telecommunication

CIGRE	International Conference on Large High Voltage Electric Systems

dB	Decibel

dBA	Decibel Absolute

DC	Direct Current

deg C	Degrees Celsius

DG	Diesel Generator

DOT	Department of Telecommunication

DSCA	Distribution, Switching, Control, Alarm and Monitoring

e.m.f.	Electro motive force

EMI	Electro Magnetic Interference

FET	Field Effect Transistor

FSD	Full Scale Deflection

FR/FC	Float Rectifier cum Float Charger

FR/BC	Float Rectifier cum Battery Charger

GR	Generic Requirements

IEC	International Electro-technical Commission

IS	Indian Standards

ISO	International Organisation for Standardisation

Kg	Kilo Grams

KHz	Kilo Hertz

LCD	Liquid Crystal Device

LED	Light Emitting Diodes

LPZ	Light Protection Zone

MHz	Mega Hertz

MIB	Management Information Base

MOV	Metal Oxide Varistor

MTBF	Mean Time between Failures

ms	milli seconds

PCB	Printed Circuit Board

PF	Power factor

QA	Quality Assurance

QM	Quality Manual

RFI	Radio Frequency Interference

RTEC	Regional Telecom Engineering Centre

SMPS	Switch Mode Power Supply

T & D	Technical & Development

Uw	Impulse Withstand Voltage

V	Volts

VDE	Verband Der Elektrootechniker

VRLA	Valve Regulated Lead Acid

***********